## Sheet2
LCD display voltmeter communication protocol					Command 6 bytes plus CRC16/MODBUS

Address type	Address meaning	Decimal address	Hexadecimal address		gain	Remark		Read register1	Read multiple registers	Write registers and data
Data address / （1-99）	Write parameter password	0	0	R		0XAABB	0XAABB	TX: 02 03 00 00 00 01 84 39 / RX: 02 03 02 AA BB C2 97
	Rated voltage	1	1	R	100	220.00 V	220.00V	TX: 02 03 00 01 00 01 D5 F9 / RX: 02 03 02 55 F0 C3 50		55F0->(DEC)22000
	Rated current	2	2	R	1000	5000A	5.000A	TX: 02 03 00 02 00 01 25 F9 / RX: 02 03 02 13 88 F1 12		1388→(DEC)5000
	Active power under 0.5L	3	3	R	1	5500	550.0W	TX: 02 03 00 03 00 01 74 39 / RX: 02 03 02 15 7C F3 35		157C→(DEC)5500
	Reactive power under 0.5L	4	4	R	1	9526	952.6VAR	TX: 02 03 00 04 00 01 C5 F8 / RX: 02 03 02 25 36 66 C2		2536→(DEC)598---???not 1726(HEC)=9526(DEC)
Version	Hardware version low	5	5	R		00-00	D17B	TX: 02 03 00 05 00 01 94 38 / RX: 02 03 02 D1 7B E0 37	TX: 02 03 00 05 00 02 D4 39 / RX: 02 03 04 D1 7B 01 BA 00 35
	High hardware version	6	6	R		00-00	01BA	TX: 02 03 00 06 00 01 64 38 / RX: 02 03 02 01 BA 7C 67
	Software version low	7	7	R		00-01	1D06	TX: 02 03 00 07 00 01 35 F8 / RX: 02 03 02 1D 06 75 16
	Software version high	8	8	R		01-00	'0203	TX: 02 03 00 08 00 01 05 FB / RX: 02 03 02 02 03 BD 25
	Protocol version number low	9	9	R		00-02	6400	TX: 02 03 00 09 00 01 54 3B / RX: 02 03 02 64 00 D6 84
	Protocol version number high	10	A	R		00-00	0203	TX: 02 03 00 0A 00 01 A4 3B / RX: 02 03 02 02 03 BD 25
	Module type	11	B	R		0X1011	6400	TX: 02 03 00 0B 00 01 F5 FB / RX: 02 03 02 64 00 D6 84
	Communication address & baud rate status word	12	C	R		0X0203（Address is0X03）	0203	TX: 02 03 00 0C 00 01 44 3A / RX: 02 03 02 02 03 BD 25
	Pulse constant	13	D	R		0X3200	6400	TX: 02 03 00 0D 00 01 15 FA / RX: 02 03 02 64 00 D6 84
Electrical parameters	Channel voltage	14	E	R	10	Channel 2 voltage value, unit V 0.1V	220.0V	TX: 02 03 00 0E 00 01 E5 FA / RX: 02 03 02 08 98 FA 2E		0898→(DEC)2200
	Channel current low L	15	F	R	1000	Channel 2 current value, unit A 0.001A	4.999A	TX: 02 03 00 0F 00 01 B4 3A / RX: 02 03 02 13 87 B1 16	TX: 02 03 00 0F 00 02 F4 3B / RX: 02 03 04 13 88 00 00 4D 9D
	Channel current high H	16	10	R				TX: 02 03 00 10 00 01 85 FC / RX: 02 03 02 00 00 FC 44
	Channel active power low 1_3_4	17	11	R	10	Channel active power value, unit: w 0.1W	562.3W	TX: 02 03 00 11 00 01 D4 3C / RX: 02 03 02 15 F7 B3 52	TX: 02 03 00 11 00 02 94 3D / RX: 02 03 04 15 F5 00 00 DD 0D	15F7→5623
	Channel active power high 1_3_4	18	12	R		Channel active power value, unit: w		TX: 02 03 00 12 00 01 24 3C / RX: 02 03 02 00 00 FC 44
	Channel reactive power low 1_3_4	19	13	R	10	Channel reactive power value, unit: var 0.1VAR	170.5VAR	TX: 02 03 00 13 00 01 75 FC / RX: 02 03 02 06 A9 3F 9A	TX: 02 03 00 13 00 02 35 FD / RX: 02 03 04 06 A9 00 00 19 9B	06A9→1705
	Channel reactive power high 1_3_4	20	14	R		Channel reactive power value, unit: var		TX: 02 03 00 14 00 01 C4 3D / RX: 02 03 02 00 00 FC 44
	Channel apparent power low 1_3_4	21	15	R	10	Channel apparent power value, unit: ah 0.1AH	587.6AH	TX: 02 03 00 15 00 01 95 FD / RX: 02 03 02 16 F4 F3 A3	TX: 02 03 00 15 00 02 D5 FC / RX: 02 03 04 16 F4 00 00 8C 89
	Channel apparent power high 1_3_4	22	16	R		Channel apparent power value, unit: ah / 0.1AH, This should be units of VA		TX: 02 03 00 16 00 01 65 FD / RX: 02 03 02 00 00 FC 44
	Channel 1 energy low 1_3_3	23	17	R	1	Channel active energy value, unit: wh 1WH	519WH	TX: 02 03 00 17 00 01 34 3D / RX: 02 03 02 02 07 BC E6	TX: 02 03 00 17 00 02 74 3C / RX: 02 03 04 02 0A 00 00 E8 89	0207→(DEC)=519
	Channel 1 energy high 1_3_3	24	18	R		Active energy value of the channel, unit: wh		TX: 02 03 00 18 00 01 04 3E / RX: 02 03 02 00 00 FC 44
	operating hours	25	19	R	1	Channel working time, unit: M minutes	94 M	TX: 02 03 00 19 00 01 55 FE / RX: 02 03 02 00 5E 7D BC		005E→(DEC)=94
	The current external temperature of the module Operating time in minutes	26	1A	R	100	External temperature of the channel, unit: degree	25℃	TX: 02 03 00 1A 00 01 A5 FE / RX: 02 03 02 00 19 3D 8E		0019→(DEC)=25
	Current internal temperature	27	1B	R	1	Channel internal temperature, unit: degree	没有意义->Pointless not supported	TX: 02 03 00 1B 00 01 F4 3E / RX: 02 03 02 B7 0D 4A 71
	RTC battery voltage	28	1C	R	10	RTC battery voltage unit:V	没有意义->Pointless not supported	TX: 02 03 00 1C 00 01 45 FF / RX: 02 03 02 00 00 FC 44
	Power factor	29	1D	R	100	0.01 1.00- 0.50	F	TX: 02 03 00 1D 00 01 14 3F / RX: 02 03 02 00 5F BC 7C		005F→(DEC)=95
	Voltage frequency	30	1E	R	100	HZ 50.00HZ	50.00HZ	TX: 02 03 00 1E 00 01 E4 3F / RX: 02 03 02 01 F4 FC 53		01F4→(DEC) 500
	Alarm status word	31	1F	R	1	bit0：Channel 1 overvoltage； / bit1：Channel 1 overcurrent； / bit2：Channel 1 overpower； / bit3：Channel 1 overpower； / bit4：Passage through external temperature； / bit5：Work outdated； / Bit6：over the internal temperature.		TX: 02 03 00 1F 00 01 B5 FF / RX: 02 03 02 63 80 D5 14
RTC clock	year	40	28	R/W	1			TX: 02 03 00 28 00 06 45 F3 / RX: 02 03 0C 00 00 00 01 00 01 00 00 00 23 00 0D FD 2E			TX: 02 10 00 28 00 01 00 01 02 07 E6 ?? ?? my guess	07 E6 2022 year. 0028 command word, 0001 write addr register, 02 bytes to write, 07E6 year data for 2022.
	month	41	29	R/W	1					TX: 02 10 00 28 00 03 06 07 E6 00 01 00 16	07E6→2022, 0001, Jan, 0016, 22 day
	day	42	2A	R/W	1
	Hour	43	2B	R/W	1
	Minute	44	2C	R/W	1
	Second	45	2D	R/W	1
Alarm parameter	temperature	50	32	R/W		Set the channel temperature alarm threshold	170	TX: 02 03 00 32 00 01 25 F6 / RX: 02 03 02 00 AA 7C 3B
	Voltage threshold	51	33	R/W	10	Set the channel overvoltage alarm threshold 0.1V	277.0V	TX: 02 03 00 33 00 01 74 36 / RX: 02 03 02 0A D2 7A B9		0AD2_>2770 / 295.0v	TX: 02 10 00 33 00 01 02 0B 86 31 F1 / RX: 02 10 00 33 00 4D F0	0B86→2950dec
	Current threshold L	52	34	R/W	1000	Set the channel overcurrent alarm threshold 0.001A	0A	TX: 02 03 00 34 00 01 C5 F7 / RX: 02 03 02 00 00 FC 44	TX: 02 03 00 34 00 02 85 F6 / RX: 02 03 04 00 00 00 00 C9 33	5640.756A	TX: 02 10 00 34 00 02 04 12 34 00 56 3A 84 / RX: 02 10 00 34 00 4F C0
	Current threshold H	53	35	R/W	1000	Set the channel overcurrent alarm threshold 0.001A		TX: 02 03 00 35 00 01 94 37 / RX: 02 03 02 00 00 FC 44		0X00561234
	Power threshold L	54	36	R/W	9	Set the channel power alarm threshold to 0.1W	200000.0W	TX: 02 03 00 36 00 01 64 37 / RX: 02 03 02 84 80 9E E4	TX: 02 03 00 36 00 02 24 36 / RX: 02 03 04 84 80 00 1E 60 23	7437.6W	TX: 02 10 00 36 00 02 04 22 88 00 01 34 47 / RX: 02 10 00 36 00 4E A0	84 80 00 1E-→ 001E8480 → 2000.000 W
	Power threshold H	55	37	R/W	10	Set the channel power alarm threshold to 0.1W		TX: 02 03 00 37 00 01 35 F7 / RX: 02 03 02 00 1E 7C 4C		0X00012288
	Time threshold L	56	38	R/W		Set the channel time alarm threshold 1 minute	120:13 小时：分钟 hours: Minutes	TX: 02 03 00 38 00 01 05 F4 / RX: 02 03 02 27 10 E6 78	TX: 02 03 00 38 00 02 45 F5 / RX: 02 03 04 2E ED 00 00 50 2E	22554 =225hours 54 minutes	TX: 02 10 00 38 00 02 04 58 1A 00 00 CC FE / RX: 02 10 00 38 00 4A C0
	Time threshold H	57	39	R/W		Set the channel time alarm threshold 1 minute		TX: 02 03 00 39 00 01 54 34 / RX: 02 03 02 00 00 FC 44		0x581A 写数据时分钟不能大于60 the minutes cannot be greater than when writing data
	Power threshold L	58	3A	R/W	999	Set the channel energy alarm threshold 0.001KWH	1000.000KWH	TX: 02 03 00 3A 00 01 A4 34 / RX: 02 03 02 42 40 CD 14	TX: 02 03 00 3A 00 02 E4 35 / RX: 02 03 04 42 40 00 0F 9C 9B	3346.722KWH	TX: 02 10 00 3A 00 02 04 11 22 00 33 9A A3 / RX: 02 10 00 3A 00 4B A0	00 0F 42 40-→ hex to 1000.000 dec
	Power threshold H	59	3B	R/W	1000	Set the channel energy alarm threshold 0.001KWH		TX: 02 03 00 3B 00 01 F5 F4 / RX: 02 03 02 00 0F BC 40		0x331122		00 33 11 22 -→hex to 3346.722 WH dec
	Channel opening time 1	60	3C			Turn on channel 2 power supply at the set time point 1
	Channel closing time 1	61	3D			Turn off channel 2 power supply at the set time point 1
	Channel opening time 2	62	3E			Turn on channel 2 power supply at the set time point 2
	Channel closing time 2	63	3F			Turn off channel 2 power supply at the set time point 2
	Channel opening time 3	64	40			Turn on channel 2 power supply at the set time point 3
	Channel closing time 3	65	41			Turn off channel 2 power supply at the set time point 3
	Channel opening time 4	66	42			Turn on channel 2 power supply at the set time point 4
	Channel closing time 4	67	43			Turn off channel 2 power supply at the set time point 4
	Time switch configuration	68	44			0: off, 1: on
Instruction address / （150~200）	Channel 1 control instruction 2_13	69	45			0: off, 1: on
	Channel 2 control instruction 2_14	70	46			0: off, 1: on
	Channel 1 energy low 1_3_3	340	154	W	1	Channel active energy value, unit: wh 1WH	519WH			Write data00	TX: 02 10 01 54 00 02 04 00 00 00 00 F5 B4 / RX: 02 10 01 54 00 36 00	0x0154 clear energy command word
	Channel 1 energy high 1_3_3	341	155	W		Active energy value of the channel, unit: wh
	Channel 1 energy mantissa low 1_3_3	342	156	W					Write data00	TX: 02 10 01 56 00 02 04 00 00 00 00 74 6D / RX: 02 10 01 56 00 37 60
	Channel 1 energy mantissa high 1_3_3	343	157	W
	working time	344	158	W	1	Channel working time, unit: M minutes	94 M			Write data00	TX: 02 10 01 58 00 01 02 00 00 AF 78 / RX: 02 10 01 58 00 33 00	0x0158 4 clear time command word

Note: / Slave address: 2 / Baud rate：9600 TX 02 03 00 00 00 0E C5 EC
6. Get the software date and version number
JUNK!	06 03 00 FE 71 2C
TX: 06 03 00 FE 71 2C
RX: 06 03 09 0D 32 30 32 30 5F 30 38 32 31 5F 56 31 30 7D 2C